## Links - COA 1
Annexure -COA1
List of outages of Communication Links, approved to avail during the month of
2021-01-01
[11 empty] | Dated : | 2020-12-29
A | Details of Communication Links (Point to Point), proposed : | [9 empty] | Communication VC Date : | 2020-12-29
SL | Name of Requesting Agency | Description of Link | Source | Destination | Channel Routing/Alternate channel status | Ownership/Cordinating agencies | Reason for availing outage & Precautions / actions being taken to ensure communication system availability | Outage proposed from | Outage proposed upto | Total hours of outage proposed now | Approved ? (Y/N) | RPC Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| PGCIL SR 1 | NIL
PGCIL SR 2
1 | PGCIL SR-II | 101 RTU data Tuticorin PS- Madhurai DCPC SRLDC | Tuticorin PS | Madhurai DCPC SRLDC | NOT available | PGCIL | Relocation of equipment at Tuticorin PS | Shall be done as and when Kudankulam shutdown is available |  | #VALUE! | N | To be applied with specific dates
2 | PGCIL SR-II | All SR2 & SR1 Links | Somanahalli PGCIL | SRLDC | All | PGCIL | Shifting of SDH Equipments in Somanahalli PGCIL | Shall be done upon completion of civil construction |  | #VALUE! | N | To be applied with specific dates
APTRANSCO
1 | APTRANSCO | HVDC-II signal for tripping Kalyandurg feeder at 220KV Anantapur | Kolar PGCIL, Karnataka | 220KVSS Anantapur | Kolar PGCIL - Somanahalli PGCIL-BidadiPGCIL - Nelamangala KPTCL- Hirayur PGCIL- Pavagada PG- Gooty PGCIL - Gooty Sw.St 220KV-Anantapur220KVSS | APTRANSCO/ PGCI/SRLDC | Shifting of Tejas SDH equipment (APTRANSCO COD4 Sr.No.102) and Valiant PDH equipment /MUX (APTRANSCO COD4 Sr.No.103) to new Communication room | 2021-01-06 09:00 | 2021-01-06 21:00 | 12:00 | Y | (Sl.No: 57 from the Database)
2 | APTRANSCO | Kudamkulam -II signal for tripping PTR at 220KVSS Anantapur. | Kolar PGCIL, Karnataka | 220KVSS Anantapur | Kolar PGCIL - Somanahalli PGCIL-BidadiPGCIL - Nelamangala KPTCL- Hirayur PGCIL- Pavagada PGCIL- Gooty PGCIL - Gooty Sw.St 220KV-Anantapur 220KVSS | APTRANSCO/ PGCI/SRLDC | Shifting of Tejas SDH equipment (APTRANSCO COD4 Sr.No.102) and Valiant PDH equipment /MUX (APTRANSCO COD4 Sr.No.103) to new Communication room | 2021-01-06 09:00 | 2021-01-06 21:00 | 12:00 | Y | (Sl.No: 58 from the Database)
3 | APTRANSCO | HVDC-I signal for tripping 132KV Vempalli , 132KV Pulivendula & 132KV Proddatur - 1 & II at 220KVSS Yerraguntla. | Kolar PGCIL, Karnataka | 220KV SS Yerraguntla | Kolar PGCIL - Somanahalli PGCIL-BidadiPGCIL - Nelamangala KPTCL- Hirayur PGCIL- Pavagada PGCIL- Gooty PGCIL - Gooty Sw.St 220KV-C.K.Palli 220KVSS-RTPP 220KVSS- Yerraguntla 220KVSS | APTRANSCO/ PGCI/SRLDC | Shifting of Tejas SDH equipment (APTRANSCO COD4 Sr.No.102) and Valiant PDH equipment /MUX (APTRANSCO COD4 Sr.No.103) to new Communication room. Gooty to Chinakampalli alternate path shall be provided through Gooty - SYPalli-Narnoor-Satthenapalli-Podili-Nellore-Renigunta-Chinakampalli | 2021-01-06 09:00 | 2021-01-06 21:00 | 12:00 | Y | (Sl.No: 53 from the Database)
4 | APTRANSCO | Kudamkulam -I signal for tripping PTR - I&II at 220KVSS Yerraguntla. | Kolar PGCIL, Karnataka | 220KV SS Yerraguntla | Kolar PGCIL - Somanahalli PGCIL-BidadiPGCIL - Nelamangala KPTCL- Hirayur PGCIL- Pavagada PGCIL- Gooty PGCIL - Gooty Sw.St 220KV-C.K.Palli 220KV- RTPP220KV-Yerraguntla 220KVSS | APTRANSCO/ PGCI/SRLDC | Shifting of Tejas SDH equipment (APTRANSCO COD4 Sr.No.102) and Valiant PDH equipment /MUX (APTRANSCO COD4 Sr.No.103) to new Communication room. Gooty to Chinakampalli alternate path shall be provided through Gooty - SYPalli-Narnoor-Satthenapalli-Podili-Nellore-Renigunta-Chinakampalli | 2021-01-06 09:00 | 2021-01-06 21:00 | 12:00 | Y | (Sl.No: 54 from the Database)
5 | APTRANSCO | HVDC-I signal for tripping 132KV Pulivendula - I&II , 132KV Lingala & 132KV Balapanuru at 220KVSS Pulivendula. | Kolar PGCIL, Karnataka | 220KV SS Pulivendula | Kolar PGCIL - Somanahalli PGCIL-BidadiPGCIL - Nelamangala KPTCL- Hirayur PGCIL- Pavagada PGCIL- Gooty PGCIL - Gooty Sw.St 220KV-C.K.Palli 220KVSS-RTPP 220KVSS- Pulivendala 220KVSS | APTRANSCO/ PGCI/SRLDC | Shifting of Tejas SDH equipment (APTRANSCO COD4 Sr.No.102) and Valiant PDH equipment /MUX (APTRANSCO COD4 Sr.No.103) to new Communication room. Gooty to Chinakampalli alternate path shall be provided through Gooty - SYPalli-Narnoor-Satthenapalli-Podili-Nellore-Renigunta-Chinakampalli | 2021-01-06 09:00 | 2021-01-06 21:00 | 12:00 | Y | (Sl.No: 55 from the Database)
6 | APTRANSCO | HVDC-I signal for tripping 132KV Madanapalli feeders -I,II&III at 220KV Madanapalli | Kolar PGCIL, Karnataka | 220KVSS Madanapalli | Kolar PGCIL - Somanahalli PGCIL-BidadiPGCIL - Nelamangala KPTCL- Hirayur PGCIL- Pavagada PGCIL- Gooty PGCIL - Gooty Sw.St 220KV-C.K.Palli 220KVSS-Kalikiri 220KVSS-Madanapalli 220KVSS | APTRANSCO/ PGCI/SRLDC | Shifting of Tejas SDH equipment (APTRANSCO COD4 Sr.No.102) and Valiant PDH equipment /MUX (APTRANSCO COD4 Sr.No.103) to new Communication room. Gooty to Chinakampalli alternate path shall be provided through Gooty - SYPalli-Narnoor-Satthenapalli-Podili-Nellore-Renigunta-Chinakampalli | 2021-01-06 09:00 | 2021-01-06 21:00 | 12:00 | Y | (Sl.No: 56 from the Database)
7 | APTRANSCO | HVDC-III for tripping Moolavanka PTR-I&II and 132KV Rayachoty feeder at 220KVSS C.K.Palli | Kolar PGCIL, Karnataka | 220KVSS CKPalli | Kolar PGCIL - Somanahalli PGCIL-Bidadi PGCIL- Nelamangala KPTCL- Hirayur PGCIL- Pavagada PGCIL- Gooty PGCIL - Gooty Sw.St 220KV- C.K.Palli 220KVSS | APTRANSCO/ PGCI/SRLDC | Shifting of Tejas SDH equipment (APTRANSCO COD4 Sr.No.102) and Valiant PDH equipment /MUX (APTRANSCO COD4 Sr.No.103) to new Communication room. Gooty to Chinakampalli alternate path shall be provided through Gooty - SYPalli-Narnoor-Satthenapalli-Podili-Nellore-Renigunta-Chinakampalli | 2021-01-06 09:00 | 2021-01-06 21:00 | 12:00 | Y | (Sl.No: 62 from the Database)
8 | APTRANSCO | Kudamkulam -I signal for tripping 132 KV SS Badvel feeder at Vontimitta 132KVSS | Kolar PGCIL, Karnataka | 132 KV SS Vontimitta | Kolar PGCIL - Somanahalli PGCIL-BidadiPGCIL - Nelamangala KPTCL- Hirayur PGCIL- Pavagada PGCIL- Gooty PGCIL - Gooty Sw.St 220KV-C.K.Palli 220KV-Kadapa 220KV-Vontimitta 132KVSS | APTRANSCO/ PGCI/SRLDC | Shifting of Tejas SDH equipment (APTRANSCO COD4 Sr.No.102) and Valiant PDH equipment /MUX (APTRANSCO COD4 Sr.No.103) to new Communication room. Gooty to Chinakampalli alternate path shall be provided through Gooty - SYPalli-Narnoor-Satthenapalli-Podili-Nellore-Renigunta-Chinakampalli | 2021-01-06 09:00 | 2021-01-06 21:00 | 12:00 | Y | (Sl.No: 63 from the Database)
9 | APTRANSCO | Kudamkulam -I signal for tripping PTR-I,II,III at 220KVSS Kalikiri. | Kolar PGCIL, Karnataka | 220KVSS Kalikiri | Kolar PGCIL - Somanahalli PGCIL-BidadiPGCIL - Nelamangala KPTCL- Hirayur PGCIL- Pavagada PGCIL- Gooty PGCIL - Gooty Sw.St 220KV-C.K.Palli 220KV-Kalikiri 220KVSS | APTRANSCO/ PGCI/SRLDC | Shifting of Tejas SDH equipment (APTRANSCO COD4 Sr.No.102) and Valiant PDH equipment /MUX (APTRANSCO COD4 Sr.No.103) to new Communication room. Gooty to Chinakampalli alternate path shall be provided through Gooty - SYPalli-Narnoor-Satthenapalli-Podili-Nellore-Renigunta-Chinakampalli | 2021-01-06 09:00 | 2021-01-06 21:00 | 12:00 | Y | (Sl.No: 64 from the Database)
KPTCL
1 | KPTCL | VSAT communication link | SCADA HUB | All the station SCADA data | Alternate channel being testing | KPTCL | VSAT & HUB maintainance and switchover from MCC to BCC | 2021-01-06 12:30 | 2021-01-06 13:00 | 00:30 | Y
2 | KPTCL | VSAT communication link | SCADA HUB | All the station SCADA data | Alternate channel being testing | KPTCL | VSAT & HUB maintainance and switchover from MCC to BCC | 2021-01-27 12:30 | 2021-01-27 13:00 | 00:30 | Y
KSEBL
1 | KSEBL | Alcatel IP Exchange Channel (E1) | Thiruvananthapuram | Bangalore | Nil | KSEBL | Preventive Manintenance at Kalamassery SDH | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | (Sl.No:1 from Database)
2 | KSEBL | Alcatel IP Exchange Channel (E1) | Kalamassery | Thiruvananthapuram | Nil | KSEBL | Preventive Manintenance at Kalamassery SDH | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | (Sl.No:2 from Database)
3 | KSEBL | Alcatel IP Exchange Channel (E1) | Kalamassery | Bangalore | Nil | KSEBL | Preventive Manintenance at Kalamassery SDH | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | (Sl.No:3 from Database)
4 | KSEBL | ICCP Main Ring (Ethernet) | Kalamassery | Bangalore | Nil | KSEBL | Preventive Manintenance at Kalamassery SDH | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | (Sl.No:4 from Database) KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
5 | KSEBL | ICCP Direct (Ethernet) | Kalamassery | Bangalore | Nil | KSEBL | Preventive Manintenance at Kalamassery SDH | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | (Sl.No:5 from Database) KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
6 | KSEBL | ICCP Main Ethernet | Thiruvananthapuram | Kalamassery | Nil | KSEBL | Preventive Manintenance at Kalamassery SDH | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | (Sl.No:7 from Database) KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
7 | KSEBL | ICCP Backup Ethernet | Thiruvananthapuram | Kalamassery | Nil | KSEBL | Preventive Manintenance at Kalamassery SDH | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | (Sl.No:8 from Database) KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
8 | KSEBL | GE PMU (URTDSM) | Kalamassery | Bangalore | Nil | KSEBL | Preventive Manintenance at Kalamassery SDH | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | (Sl.No:9 from Database)
9 | KSEBL | VCL Protection Coupler (E1) | Edamon | Selam | Nil | KSEBL/ PGCIL | Preventive Manintenance at Kalamassery SDH | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | (Sl.No:11 from Database)
10 | KSEBL | ABB NSD 70 (64 kbps) | Edappon | Kolar | Nil | KSEBL / PGCIL | Preventive Manintenance at Kalamassery SDH | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | (Sl.No:16 from Database)
11 | KSEBL | ABB NSD 70 (64 kbps) | Pallom | Kolar | Nil | KSEBL / PGCIL | Preventive Manintenance at Kalamassery SDH | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | (Sl.No:17 from Database)
12 | KSEBL | Video Conference | Kalamassery | Bangalore | Nil | KSEBL | Preventive Manintenance at Kalamassery SDH | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | (Sl.No:20 from Database)
13 | KSEBL | Video Conference | Kalamassery | Thiruvananthapuram | Nil | KSEBL | Preventive Manintenance at Kalamassery SDH | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | (Sl.No:21 from Database)
14 | KSEBL | Alcatel IP Exchange Channel (E1) | Kalamassery | Bangalore | Nil | KSEBL | Preventive Manintenance at Madakkathara SDH | 2021-01-18 11:00 | 2021-01-18 12:00 | 01:00 | Y | (Sl.No:1 from Database)
15 | KSEBL | ICCP Main Ring (Ethernet) | Kalamassery | Bangalore | Nil | KSEBL | Preventive Manintenance at Madakkathara SDH | 2021-01-18 11:00 | 2021-01-18 12:00 | 01:00 | Y | (Sl.No:4 from Database) KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
16 | KSEBL | ICCP Direct (Ethernet) | Kalamassery | Bangalore | Nil | KSEBL | Preventive Manintenance at Madakkathara SDH | 2021-01-18 11:00 | 2021-01-18 12:00 | 01:00 | Y | (Sl.No:5 from Database) KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
17 | KSEBL | VCL Protection Coupler (E1) | Shornur | Selam | Nil | KSEBL/ PGCIL | Preventive Manintenance at Madakkathara SDH | 2021-01-18 11:00 | 2021-01-18 12:00 | 01:00 | Y | (Sl.No:13 from Database)
18 | KSEBL | VCL Protection Coupler (E1) | Chalakudy | Selam | Nil | KSEBL/ PGCIL | Preventive Manintenance at Madakkathara SDH | 2021-01-18 11:00 | 2021-01-18 12:00 | 01:00 | Y | (Sl.No:15 from Database)
19 | KSEBL | DIP 5000 (64kbps) | Madakkathara | Kolar | Nil | KSEBL/ PGCIL | Preventive Manintenance at Madakkathara SDH | 2021-01-18 11:00 | 2021-01-18 12:00 | 01:00 | Y | (Sl.No:18 from Database)
20 | KSEBL | DIP 5000 (64kbps) | Kanhirode | Kolar | Nil | KSEBL/ PGCIL | Preventive Manintenance at Madakkathara SDH | 2021-01-18 11:00 | 2021-01-18 12:00 | 01:00 | Y | (Sl.No:19 from Database)
21 | KSEBL | Video Conference | Kalamassery | Bangalore | Nil | KSEBL | Preventive Manintenance at Madakkathara SDH | 2021-01-18 11:00 | 2021-01-18 12:00 | 01:00 | Y | (Sl.No:20 from Database)
22 | KSEBL | Alcatel IP Exchange Channel (E1) | Kalamassery | Bangalore | Nil | KSEBL | Shifting of Communication room Chalakudy | 2021-01-21 08:30 | 2021-01-21 17:00 | 08:30 | Y | (Sl.No:3 from Database)
23 | KSEBL | ICCP Main Ring (Ethernet) | Kalamassery | Bangalore | Nil | KSEBL | Shifting of Communication room Chalakudy | 2021-01-21 08:30 | 2021-01-21 17:00 | 08:30 | Y | (Sl.No:4 from Database) KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
24 | KSEBL | ICCP Direct (Ethernet) | Kalamassery | Bangalore | Nil | KSEBL | Shifting of Communication room Chalakudy | 2021-01-21 08:30 | 2021-01-21 17:00 | 08:30 | Y | (Sl.No:5 from Database) KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
25 | KSEBL | VCL Protection Coupler (E1) | Chalakudy | Selam | Nil | KSEBL/ PGCIL | Shifting of Communication room Chalakudy | 2021-01-21 08:30 | 2021-01-21 17:00 | 08:30 | Y | (Sl.No:15 from Database)
26 | KSEBL | Video Conference | Kalamassery | Bangalore | Nil | KSEBL | Shifting of Communication room Chalakudy | 2021-01-21 08:30 | 2021-01-21 17:00 | 08:30 | Y | (Sl.No:20 from Database)
TANTRANSCO
1 | TANTRANSCO | Neyveli-Echangadu(F.O) | Neyveli | Echangadu | Poiyur-Through PLCC/ In service | TNEB/M/s Sterlite | OPGW punctuted on 02.06.2020 due to line fault and under breakdown & rectification expected by guarantor(M/s STERLITE) | Not Updated | Not Updated | #VALUE! | N | To be applied with specific dates
2 | TANTRANSCO | Pugalur-Kalivanthapattu(F.O) | Pugalur | Kalivanthapattu | Nil | PGCIL | Rectification of Splice loss in splicing point location No: 549 Diamond formation in coordination with PGCIL | Not Updated | Not Updated | #VALUE! | N | To be applied with specific dates
3 | TANTRANSCO | Protection (TK1 SPS signals (PLCC-Ingur230KV SS to Thingalore 230KV SS) may be affected during failure) Sl.No 92 in TANTRANSCO list | Thingalore 230KV SS | Kolar | Thingalore230-Ingur230-Erode-Salem230-Salem(PG) N/w No alternate channel available | TANTRANSCO | Maintenance work | 2021-01-20 10:00 | 2021-01-20 14:00 | 04:00 | Y | (SL.No:92 from Database)
4 | TANTRANSCO | Not Updated |  |  |  |  | Shoolagiri PGCIL-Vinnamangalam 230 kv feeder under LC to make it LILO at NEW Thirupathur 230 kv ss | 2020-12-15 09:00 | 2020-12-15 17:00 | 08:00 | N | (Date is Tentative and subject to change depending on completion of work) May be applied with complete details
| TSTRANSCO | NIL
PED
1 | PED, Puducherry | Data/Voice, PLCC - OFC | Thirubuvanai | Pondy SCC | Thirubuvanai – Villianur 230 – Pondy SCC | PED, Puducherry | Preventive Maintenance. 110KV Thirubuvanai power flow data would be available from Villianur 230KV RTU | 2021-01-07 10:00 | 2021-01-07 13:00 | 03:00 | Y | (Sl.No:3 from Database)
2 | PED, Puducherry | Data/Voice, PLCC - PLCC - OFC | Eripakkam | Pondy SCC | Eripakkam – Thirubuvanai – Villianur 230 – Pondy SCC | PED, Puducherry | Preventive Maintenance. 110KV Eripakkam power flow data would be available from Villianur 230KV RTU | 2021-01-28 10:00 | 2021-01-28 13:00 | 03:00 | Y | (Sl.No:2 from Database)

## Equipment - COA 2
Annexure - COA2
List of outages of Communication Equipment, approved to avail during the month of
2021-01-01
[11 empty] | Dated : | 2020-12-29
B | Details of Communication Equipment, proposed : | [9 empty] | Communication VC Date : | 2020-12-29
SL | Name of Requesting Agency | Name of the communication equipment | Location of the Equipment / Name of Station | Name of the Channel / Path / directions, affected | Alternate Channel / Path available (Furnish details) | Ownership/Cordinating agencies | Reason for availing outage and precautions / actions being taken to ensure communication system availability | Outage proposed from | Outage proposed upto | Total hours of outage proposed now | Approved ? (Y/N) | RPC Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| PGCIL SR 1 | NIL | [7 empty] | 00:00
PGCIL SR 2
1 | PGCIL SR-II | Tejas SDH TJ1400 STM4 | Tuticorin PS | 101 RTU data Tuticorin PS- Madurai DCPC SRLDC | From Madurai alternate path will be availabel | PGCIL | Relocation of equipment at Tuticorin PS | Shall be done as and when Kudankulam shutdown is available |  | #VALUE! | N | To be applied with specific dates
2 | PGCIL SR-II | Tejas SDH TJ1400 STM16 (Sl.No:7 from Database) | Somanahalli PGCIL | All SR2 & SR1 Links | -- | PGCIL | Shifting of SDH Equipments in Somanahalli PGCIL | Shall be done upon completion of civil construction |  | #VALUE! | N | To be applied with specific dates
APTRANSCO
1 | APTRANSCO | SDH , (Tejas , TJ1400) | ANANTAPUR | Gooty-Chinakampalli | Gooty to Chinakampalli alternate path provided through Gooty - SYPalli-Narnoor-Satthenapalli-Podili-Nellore-Renigunta-Chinakampalli | APTransco | Shifting of Tejas SDH equipment (APTRANSCO COD4 Sr.No.102) to new Communication room. Gooty to Chinakampalli alternate path shall be provided through Gooty - SYPalli-Narnoor-Satthenapalli-Podili-Nellore-Renigunta-Chinakampalli | 2021-01-06 09:00 | 2021-01-06 21:00 | 12:00 | Y | (Sl.No:102 from Database)
2 | APTRANSCO | PDH, (Valiant, VCL-MX) | ANANTAPUR | Gooty-Anantapur |  | APTransco | Shifting of and Valiant PDH equipment /MUX (APTRANSCO COD4 Sr.No.103) to new PLCC room | 2021-01-06 09:00 | 2021-01-06 21:00 | 12:00 | Y | (Sl.No:103 from Database)
KPTCL
1 | KPTCL | VSAT | SCADA HUB | All the station SCADA data | Alternate channel being tested | KPTCL | VSAT & HUB maintainance and switchover from MCC to BCC | 2021-01-06 12:30 | 2021-01-06 13:00 | 00:30 | Y | (Sl.No:55 from DataBase)
2 | KPTCL | VSAT | SCADA HUB | All the station SCADA data | Alternate channel being tested | KPTCL | VSAT & HUB maintainance and switchover from MCC to BCC | 2021-01-27 12:30 | 2021-01-27 13:00 | 00:30 | Y | (Sl.No:55 from DataBase)
KSEBL
1 | KSEBL | DC Charger I (AMARA RAJA 48V/50A) (Sl.No:103 from Database) | Orkkattery | NIL | NIL | KSEBL | Routine maintenance, DC supply Available from Battery.DC source 2 is available -no interruption | 2021-01-04 10:30 | 2021-01-04 12:00 | 01:30 | Y
2 | KSEBL | DC Charger II (IGATECH Charger 48V/50A ) (Sl.No:104 from Database) | Orkkattery | NIL | NIL | KSEBL | Routine maintenance, DCsupply available from Battery. DC source 1 is available -no interruption | 2021-01-04 14:30 | 2021-01-04 16:00 | 01:30 | Y
3 | KSEBL | DC Charger II (Waves Charger 48V/100A) (Sl.No:34 from Database) | Kundara | NIL | NIL | KSEBL | Routine maintenance, No interruption standby supply available | 2021-01-05 10:30 | 2021-01-05 12:30 | 02:00 | Y
4 | KSEBL | DC Charger I (Waves 48V/50A) (Sl.No:100 from Database) | Areacode | NIL | NIL | KSEBL | Routine maintenance, DC supply Available from Battery.DC source 2 is available -no interruption | 2021-01-05 10:30 | 2021-01-05 12:00 | 01:30 | Y
5 | KSEBL | DC Charger II (Waves 48V/100A) (Sl.No:101 from Database) | Areacode | NIL | NIL | KSEBL | Routine maintenance, DCsupply available from Battery. DC source 1 is available -no interruption | 2021-01-05 14:30 | 2021-01-05 16:00 | 01:30 | Y
6 | KSEBL | DC Charger I (ASCOM Charger 48V/40A) (Sl.No:92 from Database) | Madakkathara | NIL | NIL | KSEBL | Routine maintenance, No interruption standby supply available | 2021-01-05 09:30 | 2021-01-05 15:00 | 05:30 | Y
7 | KSEBL | DC Charger III (Waves Charger 48V/40A) (Sl.No:94 from Database) | Madakkathara | NIL | NIL | KSEBL | Routine maintenance, No interruption standby supply available | 2021-01-05 14:00 | 2021-01-05 17:00 | 03:00 | Y
8 | KSEBL | DC Charger I (Waves Charger 48V/100A) (Sl.No:33 from Database) | Kundara | NIL | NIL | KSEBL | Routine maintenance, No interruption standby supply available | 2021-01-06 10:30 | 2021-01-06 11:30 | 01:00 | Y
9 | KSEBL | DC Charger I (Waves Charger 48V/100A) (Sl.No:25 from Database) | Edamon | NIL | NIL | KSEBL | Routine maintenance, No interruption standby supply available | 2021-01-06 10:30 | 2021-01-06 14:30 | 04:00 | Y
10 | KSEBL | DC Charger II (Waves Charger 48V/40A) (Sl.No:93 from Database) | Madakkathara | NIL | NIL | KSEBL | Routine maintenance, No interruption standby supply available | 2021-01-06 09:30 | 2021-01-06 12:30 | 03:00 | Y
11 | KSEBL | DC Charger I (Waves Charger 48V/50A) (Sl.No:116 from Database) | Shornur | NIL | NIL | KSEBL | Routine maintenance, DC supply Available from Battery.DC source 2 is available -no interruption | 2021-01-06 10:30 | 2021-01-06 12:00 | 01:30 | Y
12 | KSEBL | DC Charger II (IGATECH Charger 48V/50A ) (Sl.No:117 from Database) | Shornur | NIL | NIL | KSEBL | Routine maintenance, DCsupply available from Battery. DC source 1 is available -no interruption | 2021-01-06 14:30 | 2021-01-06 16:00 | 01:30 | Y
13 | KSEBL | DC Charger I (ASCOM Charger 48V/50A) (Sl.No:111 from Database) | Kanhirode | NIL | NIL | KSEBL | Routine maintenance, DC supply Available from Battery.DC source 2 is available -no interruption | 2021-01-07 10:30 | 2021-01-07 12:00 | 01:30 | Y
14 | KSEBL | DC Charger II (ASCOM Charger 48V/50A) (Sl.No:112 from Database) | Kanhirode | NIL | NIL | KSEBL | Routine maintenance, DCsupply available from Battery. DC source 1 is available -no interruption | 2021-01-07 14:30 | 2021-01-07 16:00 | 01:30 | Y
15 | KSEBL | DC Charger I (ASCOM 48V/54A) (Sl.No:84 from Database) | Chalakudy | NIL | NIL | KSEBL | Routine maintenance, No interruption standby supply available | 2021-01-07 10:00 | 2021-01-07 13:00 | 03:00 | Y
16 | KSEBL | DC Charger II (Waves Charger 48V/100A ) (Sl.No:26 from Database) | Edamon | NIL | NIL | KSEBL | Routine maintenance, No interruption standby supply available | 2021-01-08 10:30 | 2021-01-08 11:30 | 01:00 | Y
17 | KSEBL | DC Charger II (Waves 48V/60A) (Sl.No:85 from Database) | Chalakudy | NIL | NIL | KSEBL | Routine maintenance, No interruption standby supply available | 2021-01-08 10:00 | 2021-01-08 13:00 | 03:00 | Y
18 | KSEBL | DC Charger I (Waves Charger 48V/100A) (Sl.No:42 from Database) | Edappon | NIL | NIL | KSEBL | Monthly maintenance- No interruption | 2021-01-11 12:00 | 2021-01-11 12:30 | 00:30 | Y
19 | KSEBL | DC Charger II (Waves Charger 48V/100A) (Sl.No:43 from Database) | Edappon | NIL | NIL | KSEBL | Routine maintenance, No interruption standby supply available | 2021-01-11 11:00 | 2021-01-11 16:00 | 05:00 | Y
20 | KSEBL | SDH TJ1400 (Sl.No:70 from Database) | Kalamassery | Towards Brahmapuram & Chalakudy | NIL | KSEBL | Preventive Maintenance of SDH Equipment at Kalamassery | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
21 | KSEBL | EPABX - BPL MDX 50 (Sl.No:73 from Database) | Kalamassery | Towards SLDC & Backup SLDC | NIL | KSEBL | Preventive Maintenance of SDH Equipment at Kalamassery | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
22 | KSEBL | GE PMU (URTDSM) (Sl.No:71 from Database) | Kalamassery | Towards SRLDC Control centre | NIL | PGCIL | Preventive Maintenance of SDH Equipment at Kalamassery | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
23 | KSEBL | Alcatel IP Exchange (Sl.No:72 from Database) | Kalamassery | Towards Banglore & Thiruvananthapuram | NIL | KSEBL | Preventive Maintenance of SDH Equipment at Kalamassery | 2021-01-11 10:30 | 2021-01-11 12:00 | 01:30 | Y | KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
24 | KSEBL | DC Charger I (Waves Charger 48V/100A) (Sl.No:14 from Database) | Pothencode | NIL | NIL | KSEBL | Monthly maintanence. No interruption as stand by available | 2021-01-11 11:00 | 2021-01-11 11:30 | 00:30 | Y
25 | KSEBL | DC Charger II (Waves Charger (Sl.No:15 from Database) | Pothencode | NIL | NIL | KSEBL | Monthly maintanence. No interruption as stand by available | 2021-01-11 11:00 | 2021-01-11 11:30 | 00:30 | Y
26 | KSEBL | DC Charger I (IGATECH Charger 48V/50A) (Sl.No:66 from Database) | Brahmapuram | NIL | NIL | KSEBL | Routine maintenance, DC supply will be Available from Battery.DC source 2 -no interruption | 2021-01-12 09:30 | 2021-01-12 13:00 | 03:30 | Y
27 | KSEBL | DC Charger II (AE Charger 48V/20A) (Sl.No:67 from Database) | Brahmapuram | NIL | NIL | KSEBL | Routine maintenance, DC supply will be Available from Battery.DC source 1 -no interruption | 2021-01-12 14:00 | 2021-01-12 17:30 | 03:30 | Y
28 | KSEBL | EPABX - INTELLICON KAREL DS 200 (Sl.No:39 from Database) | Edappon | Towards SLDC & Backup SLDC | NIL | KSEBL | Monthly maintenance- No interruption | 2021-01-12 11:00 | 2021-01-12 11:30 | 00:30 | Y
29 | KSEBL | DC Charger I (DUBAS Charger 48V/40A) (Sl.No:60 from Database) | Ambalamughal | NIL | NIL | KSEBL | Routine maintenance, DC supply will be Available from Battery.DC source 2 -no interruption | 2021-01-13 09:30 | 2021-01-13 13:00 | 03:30 | Y
30 | KSEBL | DC Charger II (DUBAS Charger 48V/40A) (Sl.No:61 from Database) | Ambalamughal | NIL | NIL | KSEBL | Routine maintenance, DC supply will be Available from Battery.DC source 1 -no interruption | 2021-01-13 14:00 | 2021-01-13 17:30 | 03:30 | Y
31 | KSEBL | DC Charger I (ASCOM Charger 48V/21A) (Sl.No:5 from Database) | Thiruvananthapuram | NIL | NIL | KSEBL | Monthly maintanence. No interruption as stand by available | 2021-01-15 10:30 | 2021-01-15 11:30 | 01:00 | Y
32 | KSEBL | SDH TJ1401 (Sl.No:86 from Database) | Madakkathara | Towards Arekode, Chalakudy & Shoranur | NIL | KSEBL | Preventive Maintenance of SDH Equipment at Madakkathara | 2021-01-18 11:00 | 2021-01-18 12:00 | 01:00 | Y
33 | KSEBL | VCL-MX PDH (Sl.No:87 from Database) | Madakkathara | Towards Kolar | NIL | KSEBL | Preventive Maintenance of SDH Equipment at Madakkathara | 2021-01-18 11:00 | 2021-01-18 12:00 | 01:00 | Y
34 | KSEBL | DIP 5000, (Sl.No:88 from Database) | Madakkathara | Towards Kolar | NIL | KSEBL | Preventive Maintenance of SDH Equipment at Madakkathara | 2021-01-18 11:00 | 2021-01-18 12:00 | 01:00 | Y
35 | KSEBL | EPABX - BPL MDX 50 (Sl.No:89 from Database) | Madakkathara | Towards SLDC & Backup SLDC | NIL | KSEBL | Preventive Maintenance of SDH Equipment at Madakkathara | 2021-01-18 11:00 | 2021-01-18 12:00 | 01:00 | Y
36 | KSEBL | DC Charger IV (Waves Charger 48V/60A) (Sl.No:77 from Database) | Kalamassery | Nil | NIL | KSEBL | Routine maintenance, DC supply will be Available from Battery.DC source 1 -no interruption | 2021-01-20 09:30 | 2021-01-20 13:00 | 03:30 | Y
37 | KSEBL | DC Charger V (Keltron Charger 66V/90A) (Sl.No:78 from Database) | Kalamassery | Nil | NIL | KSEBL | Routine maintenance, DC supply will be Available from Battery.DC source 1 -no interruption | 2021-01-20 14:00 | 2021-01-20 17:30 | 03:30 | Y
38 | KSEBL | SDH TJ1400 (Sl.No:79 from Database) | Chalakkudy | Towards Madakkathara & Kalamassery | NIL | KSEBL | Shifting of equipments to new communication room | 2021-01-21 08:30 | 2021-01-21 17:00 | 08:30 | Y | KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
39 | KSEBL | EPABX - BPL MDX 50 (Sl.No:81 from Database) | Chalakkudy | E&M Channel | NIL | KSEBL | Shifting of equipments to new communication room | 2021-01-21 08:30 | 2021-01-21 17:00 | 08:30 | Y | KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
40 | KSEBL | DC Charger I (ASCOM 48V/54A) (Sl.No:84 from Database) | Chalakkudy | NIL | NIL | KSEBL | Shifting of equipments to new communication room | 2021-01-21 08:30 | 2021-01-21 17:00 | 08:30 | Y | KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
41 | KSEBL | DC Charger II (Waves 48V/60A) (Sl.No:85 from Database) | Chalakkudy | NIL | NIL | KSEBL | Shifting of equipments to new communication room | 2021-01-21 08:30 | 2021-01-21 17:00 | 08:30 | Y | KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
42 | KSEBL | VCL Protection Coupler (Sl.No:80 from Database) | Chalakkudy | Selam | NIL | KSEBL | Shifting of equipments to new communication room | 2021-01-21 08:30 | 2021-01-21 17:00 | 08:30 | Y | KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
43 | KSEBL | DC Charger II (ASCOM Charger 48V/21A (Sl.No:82 from Database) | Thiruvananthapuram | NIL | NIL | KSEBL | Monthly maintanence. No interruption as stand by available | 2021-01-22 10:30 | 2021-01-22 11:30 | 01:00 | Y
44 | KSEBL | DC Charger III (ASCOM Charger 48V/25A) (Sl.No:16 from Database) | Pothencode | NIL | NIL | KSEBL | Monthly maintanence. No interruption as stand by available | 2021-01-25 11:00 | 2021-01-25 11:30 | 00:30 | Y
45 | KSEBL | DC Charger I (ASCOM Charger 48V/31A) (Sl.No:74 from Database) | Kalamassery | NIL | NIL | KSEBL | Monthly maintanence. No interruption as stand by available | 2021-01-27 10:30 | 2021-01-27 16:30 | 06:00 | Y | KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
46 | KSEBL | DC Charger II (ASCOM Charger 48V/31A) (Sl.No:75 from Database) | Kalamassery | NIL | NIL | KSEBL | Monthly maintanence. No interruption as stand by available | 2021-01-28 10:30 | 2021-01-28 16:30 | 06:00 | Y | KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
47 | KSEBL | DC Charger III (ELTEK Charger 48V/15A) (Sl.No:76 from Database) | Kalamassery | NIL | NIL | KSEBL | Monthly maintanence. No interruption as stand by available | 2021-01-29 10:30 | 2021-01-29 16:30 | 06:00 | Y | KSEBL may coordinate with PGCIL to reroute the Links so that drwal computation will not be affected. Approved subject to ensuring the alternate path to SRLDC
TANTRANSCO
1 | TANTRANSCO | PLCC, ABB, ETL41, TK1 SPS protection trip to Thingalore 230KV SS | Ingur 230 kV SS | Thingalore 230 kV SS | No | TANTRANSCO | Maintenance work | 2021-01-20 10:00 | 2021-01-20 14:00 | 04:00 | Y | (SL.No:72 From Database)
2 | TANTRANSCO | PLCC, ABB, ETL41, TK1 SPS protection trip | Thingalore 230 kV SS | Ingur 230 kV SS | No | TANTRANSCO | Maintenance work | 2021-01-20 10:00 | 2021-01-20 14:00 | 04:00 | Y | (SL.No:174 From Database)
| TSTRANSCO | NIL
PED
1 | PED, Puducherry | PLCC, Make : ABB, Model : ETL-41, | Thirubuvanai | PED, Puducherry | -- | PED, Puducherry | Preventive Maintenance. 110KV Thirubuvanai power flow data would be available from Villianur 230KV RTU | 2021-01-07 10:00 | 2021-01-07 13:00 | 03:00 | Y | (Sl.No:4 from Database)
2 | PED, Puducherry | PLCC, Make : ABB, Model : ETL-41, | Eripakkam | PED, Puducherry | -- | PED, Puducherry | Preventive Maintenance. 110KV Eripakkam voice would be available from Villianur 230KV, Puducherry SCC | 2021-01-28 10:00 | 2021-01-28 13:00 | 03:00 | Y | (Sl.No:1 from Database)
Format COA 2