## Links - COA 1
Annexure -COA1
List of outages of Communication Links, proposed to avail during the month of
Oct 2020
[11 empty] | Dated : | 2020-09-15
A | Details of Communication Links (Point to Point), proposed : | [9 empty] | Communication VC Date : | 2020-09-17
SL | Name of Requesting Agency | Description of Link | Source | Destination | Channel Routing/Alternate channel status | Ownership/Cordinating agencies | Reason for availing outage & Precautions / actions being taken to ensure communication system availability | Outage proposed from dd/mmm/yy, [hh] : mm | Outage proposed upto dd/mmm/yy, [hh] : mm | Total hours of outage proposed now | Approved ? (Y/N) | RPC Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| PGCIL SR 1 | NIL | [7 empty] | 00:00
| PGCIL SR 2 | NIL | [7 empty] | 00:00
| APTRANSCO | NIL | [7 empty] | 00:00
| KPTCL | NIL | [7 empty] | 00:00
| KSEBL | NIL | [7 empty] | 00:00
| TANTRANSCO | NIL | [7 empty] | 00:00
TSTRANSCO
1 |  | Mamidipally-Dindi | Mamidipally | Dindi | Traffic on Mamidipally-Dindi line (SPS Ramagundam-Kolar, SPS Gajwel- Kolar, SPSVeltoor-Kolar ),ICCP,PMU,Video Conference,and Voice channels between TS SLDC and SRLDC Alternate path is configured for the above channels:via Mamidipally-Maheswaram-Mahabubnagar400 KV(TSTRANSCO)-Raichur 400 KV-through PGCIL NW-SRLDC | TSTRANSCO | Supply, Erection, testing and Commissioning of (i) 4 Nos. 400 KV Quad bays at 400/220 KV Maheswaram SS, Rangaeddy district and (ii) LILO of both circuits of 400kV Mamidipally –Dindi TMDC line to 400KV Maheswaram SS (approx.4.5KM) on Multi Circuit Towers on Turnkey basis against specification No. e-EHVT-03/2018- 19. --> OPGW laying planned from existing Tower Location No. 341 to Maheswaram 400 KVSS (Mamidipally-Maheswaram line) and from Tower Location No.330 to Maheswaram 400KVSS (Maheswaram -Dindi line) . | 2020-10-25 08:30 | 2020-11-09 18:00 | 369:30 |  | Link not listed in the COD 3, Data Base. Channel Routing Diagram also does not show Dindi and Raichur. TSTRANSCO may kindly update their COD 3 Data Base and Network Routing Diagram accordingly.
| PED | NIL
1 | [9 empty] | 00:00
2 | [9 empty] | 00:00
3 | [9 empty] | 00:00
4 | [9 empty] | 00:00

## Equipment - COA 2
Annexure - COA2
List of outages of Communication Equipment proposed to avail during the month of
Oct 2020
[11 empty] | Dated : | 2020-09-15
B | Details of Communication Equipment, proposed : | [9 empty] | Communication VC Date : | 2020-09-17
SL | Name of Requesting Agency | Name of the communication equipment | Location of the Equipment / Name of Station | Name of the Channel / Path / directions, affected | Alternate Channel / Path available (Furnish details) | Ownership/Cordinating agencies | Reason for availing outage and precautions / actions being taken to ensure communication system availability | Outage proposed from dd/mmm/yy, [hh] : mm | Outage proposed upto dd/mmm/yy, [hh] : mm | Total hours of outage proposed now | Approved ? (Y/N) | RPC Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| PGCIL SR 1 | NIL | [7 empty] | 00:00
PGCIL SR 2
|  | Tejas SDH TJ1400 STM16 | Tuticorinn PS |  |  | PGCIL SR 2 | New Equipment Installation & shifting of old equipment | 2020-10-01 11:30 | 2020-10-01 14:30 | 03:00 |  | Sl No.78 in data Base
|  | Tejas SDH TJ1400 STM16 | Udumalpet PG |  |  | PGCIL SR 2 | New Equipment Installation & shifting of old equipment | 2020-10-06 11:30 | 2020-10-06 14:30 | 03:00 |  | Sl No.93 in data Base
|  | Tejas SDH TJ1400 STM16 | Madurai 400kV PG |  |  | PGCIL SR 2 | New Equipment Installation & shifting of old equipment | 2020-10-03 11:30 | 2020-10-03 14:30 | 03:00 |  | Sl No.96 in data Base
|  | Tejas SDH TJ1400 STM16 | Kalivanthapattu PG |  |  | PGCIL SR 2 | New Equipment Installation & shifting of old equipment | 2020-10-12 11:30 | 2020-10-12 14:30 | 03:00 |  | Sl No.100 in data Base
|  | Tejas SDH TJ1400 STM16 | Salem 400 kV PG |  |  | PGCIL SR 2 | New Equipment Installation & shifting of old equipment | 2020-10-14 11:30 | 2020-10-14 14:30 | 03:00 |  | Sl No.103 in data Base
|  | Tejas SDH TJ1400 STM16 | Pugulur/KarurPGCIL |  |  | PGCIL SR 2 | New Equipment Installation & shifting of old equipment | 2020-10-15 11:30 | 2020-10-15 14:30 | 03:00 |  | Sl No.109 in data Base
|  | Tejas SDH TJ1400 STM16 | Thiruvalam PG |  |  | PGCIL SR 2 | New Equipment Installation & shifting of old equipment | 2020-10-20 11:30 | 2020-10-20 14:30 | 03:00 |  | Sl No.112 in data Base
|  | Tejas SDH TJ1400 STM16 | Trichur PG |  |  | PGCIL SR 2 | New Equipment Installation & shifting of old equipment | 2020-10-22 11:30 | 2020-10-22 14:30 | 03:00 |  | Sl No.156 in data Base
|  | Tejas SDH TJ1400 STM16 | Tuticorin GIS |  |  | PGCIL SR 2 | New Equipment Installation & shifting of old equipment | 2020-10-25 11:30 | 2020-10-25 14:30 | 03:00 |  | Sl No.185 in data Base
| APTRANSCO | NIL | [7 empty] | 00:00
| KPTCL | NIL | [7 empty] | 00:00
| KSEBL | NIL | [7 empty] | 00:00
| TANTRANSCO | NIL | [7 empty] | 00:00
TSTRANSCO
1 |  | 48V CHARGER-1, Make : calidyne Model : 100 A(1+1) | 400 kV Malkaram SS |  |  | TSTRANSCO | Periodical Maintenance Works | 2020-10-21 13:00 | 2020-10-21 14:30 | 01:30 |  | Not found in the Data Base COD 3,4
2 |  | BATTERY BANK - 1 Rating : 48V/400AH Make : EXIDE; Model : VRLA | 400 kV Malkaram SS |  |  | TSTRANSCO | Periodical Maintenance Works | 2020-10-21 13:00 | 2020-10-21 14:30 | 01:30 |  | Not found in the Data Base COD 3,4
3 |  | 48V CHARGER-2, Make : DUBAS, Model : | 220 kV Ghanapur SS |  |  | TSTRANSCO | Periodical Maintenance Works | 2020-10-22 11:00 | 2020-10-22 12:30 | 01:30 |  | Sl No. 15 in Data Base
4 |  | 48 V DC BATTERY-2, Make : EXIDE, Model : VRLA | 220 kV Ghanapur SS |  |  | TSTRANSCO | Periodical Maintenance Works | 2020-10-22 11:00 | 2020-10-22 12:30 | 01:30 |  | Sl No. 17 in Data Base
5 |  | 48V CHARGER-1, Make : ASCOM, Model : SMPS | 400 kV Mamidipally SS |  |  | TSTRANSCO | Periodical Maintenance Works The Battery Charger will be switched off and existing loads will be on Battery Banks - 1 & 2 | 2020-10-21 11:00 | 2020-10-21 12:30 | 01:30 |  | Sl No. 20 in Data Base BATTERY CHARGER, Rating : 48V/100A, Make : AMARARAJA, Model : FCBC-1 & FCBC-2 Not matching.
6 |  | 48V CHARGER-2, Make : ASCOM, Model : SMPS | 400 kV Mamidipally SS |  |  | TSTRANSCO | Periodical Maintenance Works The Battery Charger will be switched off and existing loads will be on Battery Banks - 1 & 2 | 2020-10-21 11:00 | 2020-10-21 12:30 | 01:30 |  | Sl No. 21 in Data Base BATTERY CHARGER, Rating : 48V/100A, Make : AMARARAJA, Model : FCBC-1 & FCBC-2 Not matching.
7 |  | 48 V DC BATTERY-1, Make : AMARARAJA, Model : VRLA | 400 kV Mamidipally SS |  |  | TSTRANSCO | Periodical Maintenance Works The Battery Charger will be switched off and existing loads will be on Battery Banks - 1 & 2 | 2020-10-21 11:00 | 2020-10-21 12:30 | 01:30 |  | Sl No. 22 in Data Base
8 |  | 48 V DC BATTERY-2, Make : EXIDE, Model : | 400 kV Mamidipally SS |  |  | TSTRANSCO | Periodical Maintenance Works The Battery Charger will be switched off and existing loads will be on Battery Banks - 1 & 2 | 2020-10-21 11:00 | 2020-10-21 12:30 | 01:30 |  | Sl No. 23 in Data Base
9 |  | 48V CHARGER-1, Make : AMARARAJA, Model : | 400 kV Maheshwaram SS |  |  | TSTRANSCO | Periodical Maintenance Works The Battery Charger will be switched off and existing loads will be on Battery Banks - 1 & 2 | 2020-10-07 11:00 | 2020-10-07 12:30 | 01:30 |  | Sl No. 25 in Data Base
10 |  | 48V CHARGER-2, Make : AMARARAJA, Model : | 400 kV Maheshwaram SS |  |  | TSTRANSCO | Periodical Maintenance Works The Battery Charger will be switched off and existing loads will be on Battery Banks - 1 & 2 | 2020-10-07 11:00 | 2020-10-07 12:30 | 01:30 |  | Sl No. 26 in Data Base
11 |  | 48 V DC BATTERY-1, Make : AMARARAJA, Model : VRLA | 400 kV Maheshwaram SS |  |  | TSTRANSCO | Periodical Maintenance Works The Battery Charger will be switched off and existing loads will be on Battery Banks - 1 & 2 | 2020-10-07 11:00 | 2020-10-07 12:30 | 01:30 |  | Sl No. 27 in Data Base
12 |  | 48 V DC BATTERY-2, Make : AMARARAJA, Model : VRLA | 400 kV Maheshwaram SS |  |  | TSTRANSCO | Periodical Maintenance Works The Battery Charger will be switched off and existing loads will be on Battery Banks - 1 & 2 | 2020-10-07 11:00 | 2020-10-07 12:30 | 01:30 |  | Sl No. 28 in Data Base
13 |  | 48V CHARGER-1, Make : AMARARAJA, Model : | 400 kV Kethireddipally SS |  |  | TSTRANSCO | Periodical Maintenance Works The Battery Charger will be switched off and existing loads will be on Battery Banks - 1 & 2 | 2020-10-14 11:00 | 2020-10-14 12:30 | 01:30 |  | Not found in the Data Base COD 3,4
14 |  | 48V CHARGER-2, Make : AMARARAJA, Model : | 400 kV Kethireddipally SS |  |  | TSTRANSCO | Periodical Maintenance Works The Battery Charger will be switched off and existing loads will be on Battery Banks - 1 & 2 | 2020-10-14 11:00 | 2020-10-14 12:30 | 01:30 |  | Not found in the Data Base COD 3,4
15 |  | 48 V DC BATTERY-1, Make : AMARARAJA, Model : VRLA | 400 kV Kethireddipally SS |  |  | TSTRANSCO | Periodical Maintenance Works The Battery Charger will be switched off and existing loads will be on Battery Banks - 1 & 2 | 2020-10-14 11:00 | 2020-10-14 12:30 | 01:30 |  | Not found in the Data Base COD 3,4
16 |  | 48 V DC BATTERY-2, Make : AMARARAJA, Model : VRLA | 400 kV Kethireddipally SS |  |  | TSTRANSCO | Periodical Maintenance Works The Battery Charger will be switched off and existing loads will be on Battery Banks - 1 & 2 | 2020-10-14 11:00 | 2020-10-14 12:30 | 01:30 |  | Not found in the Data Base COD 3,4
| PED | NIL
00:00
00:00
00:00
00:00
Note on C34: Charger spec not matching. To be applied charger wise separately.
Note on C36: Charger and battery together ??? How ????